## Checklist
FDH Acceptance Certificate
Details - Checklist No: FC1LBR1FDH2QCCL91 Rev. 23
Phase: |  | Langeberg Ridge |  | Date & Time: | Mar, 5, 2025 13:52
FDA: |  | Langeberg Ridge |  | FDH: | FC1LBR1FDH2
Closest Address: |  | Langeberg Ridge |  | FDH Type: | FC1LBR1FDH2
Above Ground FDH Checklist
# | Item: | Description: |  |  | Result: | Comment
1 | Concrete | Smooth edges. No cracks or chips |  |  | Pass
2 | FDH Mounting | Bolts on all 4 sides of FDH. FDH to be sturdy. |  |  | Pass
3 | Conduit Organization | Organize each row of microducts for each route being brought into the cabinet. |  |  | Pass
4 | Duct Organizers | Attached correctly and secure. Conduit to be 2" high from organizer. Staggered height. |  |  | Pass
5 | Duct Caps | Dust caps to be installed on all conduits. |  |  | Pass
6 | Feeder Position | Feeder fiber should be brought to the left side of the cabinet and secured to the mounting plate. |  |  | Pass
7 | Feeder duct | Feeder fiber duct should be secured to top bracket. |  |  | Pass
8 | Tracer Wire | Route all tracer wires to the right of the cabinet to the busbar. |  |  | Pass
9 | Grounding Screw | Attach the grounding wire to the grounding screw. |  |  | Pass
10 | Labels | Labels to be installed on all conduits including spares |  |  | Pass
11 | Feeder Splicing | 2 loops of slack on cable. Splicing on Bottom tray. Fiber management to be neat. |  |  | Pass
12 | Splitter | Splitter to be secured in place. Tails to be routed correctly |  |  | Pass
13 | Routing components | Plastic holders to be in place on right side of splitter tray. |  |  | Pass
14 | Adapter Ports | All ports to have endcaps. |  |  | Pass
15 | Light Levels | Light levels to never exceed -22dB on output. Light level range between inputs may not vary more than -1.5dB. Splitter may not exceed input reading by -15dB. |  |  | Pass
16 | Components secured. | Screw in place for Splitter bay. Door hinges in working order. No loose components. |  |  | Pass
17 | Cleanliness | FDH clean. All debris removed in and around FDH. |  |  | Pass
Below Ground FDH Checklist
# | Item: | Description: |  |  | Result: | Comment
18 | HH Level | Handhole Level with NGL. |  |  | Pass
19 | Drainage | Crusher stone installed. |  |  | Pass
20 | Conduit Organization | Organize each row of microducts for each route being brought into the cabinet. |  |  | Pass
21 | Reducers | Reducers on all allocated conduits. |  |  | Pass
22 | End Caps | All spare conduits endcapped. |  |  | Pass
23 | FDH Mounting | Swing arm secured. All bolts installed. FDH pins to be installed to secure FDH to swing arm. |  |  | Pass
24 | Plugs | Microduct to have rubber plugs inside. |  |  | Pass
25 | Tracer Wire | Route all tracer wires to the right of the cabinet to the busbar. |  |  | Pass
26 | Labels | Labels to be installed on all conduits including spares |  |  | Pass
27 | Feeder Splicing | 2 loops of slack on cable. Splicing on Bottom tray. Fiber management to be neat. |  |  | Pass
28 | Splitter | Splitter to be secured in place. Tails to be routed correctly |  |  | Pass
29 | Adapter Ports | All ports to have endcaps. |  |  | Pass
30 | Light Levels | Light levels to never exceed -22dB on output. Light level range between inputs may not vary more than -1.5dB. Splitter may not exceed input reading by -15dB. |  |  | Pass
31 | Cleanliness | FDH clean. All debris removed in and around FDH. |  |  | Pass
Comments:
Contractor: , PMQC: , ClientQC: null
Representative Details:
| Client Representative |  | PMO Representative |  |  | Contractor Representative
|  |  | Jack Sparrow |  |  | Jack Sparrow
|  |  | Mar, 5, 2025 14:27 |  |  | Mar, 5, 2025 13:52

## Images
FDH Checklist Images
Details - Checklist No: FC1LBR1FDH2QCCL91 Rev. 23
Activity | Image 1 | Image 2 | Image 3
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31